## Sheet1
Address	Type	Bits	RW/RO	Min	Max	Default	Name	Right to modify	Main application	Description

0001	coil	1	RW	false	true	true	Cup1Control	ModbusServer	user interface	Control of Faraday Cup 1 using a pneumatic actuator; true = insert cup; false = withdraw
0002	coil	1	RO	false	true	false		N/A		Reserved
0003	coil	1	RO	false	true	N/A	Cup1Switch	LogicInputs	related to hardware	Measurement of limit switch status; true = switch pressed; false = switch released; in steady state, this status should match the value of register Cup1Control
0004	coil	1	RO	false	true	false		N/A		Reserved

0005	coil	1	RW	false	true	true	Cup2Control	ModbusServer	user interface	Control of Faraday Cup 2 using a pneumatic actuator; true = insert cup; false = withdraw
0006	coil	1	RO	false	true	N/A	ExternalInhibition	LogicInputs	related to hardware	Measurement of the external inhibit logic signal; true = inhibition enabled; false = inhibition disabled
0007	coil	1	RO	false	true	N/A	Cup2Switch	LogicInputs	related to hardware	Measurement of limit switch status; true = switch pressed; false = switch released; in steady state, this status should match the value of register Cup2Control
0008	coil	1	RO	false	true	false		N/A		Reserved

0009	coil	1	RW	false	true	true	Cup3Control	ModbusServer	user interface	Control of Faraday Cup 3 using a motor actuator; true = insert cup; false = withdraw
000A	coil	1	RO	false	true	false		N/A		Reserved
000B	coil	1	RO	false	true	N/A	Cup3Switch1	LogicInputs	related to hardware	Measurement of limit switch status; true = switch pressed; false = switch released; in steady state, this status should be equal to the negation of register Cup3Control
000C	coil	1	RO	false	true	N/A	Cup3Switch2	LogicInputs	related to hardware	Measurement of limit switch status; true = switch pressed; false = switch released; in steady state, this status should match the value of register Cup3Control

0010	coil	1	RO	false	true	N/A	Cup1RequestedState	MainFSM	internal	Command for the AuxiliaryFSM; true = insert the cup; false = withdraw the cup
0011	coil	1	RO	false	true	N/A	Cup2RequestedState	MainFSM	internal	- // -
0012	coil	1	RO	false	true	N/A	Cup3RequestedState	MainFSM	internal	- // -

0013	coil	1	RO	false	true	N/A	Cup1Steady	AuxiliaryFSMs	internal	Check whether the mechanism of the cup is in a transient state; true = steady state; false = transient state
0014	coil	1	RO	false	true	N/A	Cup2Steady	AuxiliaryFSMs	internal	- // -
0015	coil	1	RO	false	true	N/A	Cup3Steady	AuxiliaryFSMs	internal	- // -
0016	coil	1	RO	false	true	N/A	Cup1Inserted	AuxiliaryFSMs	user interface	Status of the cup; true = inserted; false = withdrawn
0017	coil	1	RO	false	true	N/A	Cup2Inserted	AuxiliaryFSMs	user interface	- // -
0018	coil	1	RO	false	true	N/A	Cup3Inserted	AuxiliaryFSMs	user interface	- // -

1000	holding reg.	16	RO	0	?	0	ErrorCode	MainFSM	user interface	Error code for the entire device (bitmap)
1001	holding reg.	16	RO	0	?	0	LastError	MainFSM	user interface	Code of the last error
1002	holding reg.	16	RW	0	?	0	ErrorStorage	MainFSM, Modbus.	user interface	A bitwise OR of all errors; can be reset via Modbus

1003	holding reg.	16	RW	1	65535	?	TimeLimitInserting1	ModbusServer	configuration	Time limit for the transient state when inserting a Faraday cup
1004	holding reg.	16	RW	1	65535	?	TimeLimitInserting2	ModbusServer	configuration	- // -
1005	holding reg.	16	RW	1	65535	?	TimeLimitInserting3	ModbusServer	configuration	- // -
1006	holding reg.	16	RW	1	65535	?	TimeLimitWithdrawing1	ModbusServer	configuration	Time limit for the transient state when withdrawing a Faraday cup
1007	holding reg.	16	RW	1	65535	?	TimeLimitWithdrawing2	ModbusServer	configuration	- // -
1008	holding reg.	16	RW	1	65535	?	TimeLimitWithdrawing3	ModbusServer	configuration	- // -

1009	holding reg.	16	RW	1	3	1	ActiveCup	MainFSM	internal	The first inserted Faraday cup as seen from the ion source side; if none is inserted, the previous value should be retained;

100A	holding reg.	16	RO	0	?	0	Cup1Error	AuxiliaryFSMs	internal	Error code for the cup mechanism (bitmap)
100B	holding reg.	16	RO	0	?	0	Cup2Error	AuxiliaryFSMs	internal	- // -
100C	holding reg.	16	RO	0	?	0	Cup3Error	AuxiliaryFSMs	internal	- // -
100D	holding reg.	16	RO	0	?	0	Cup1LastError	AuxiliaryFSMs	internal	Code of the last error for the cup mechanism
100E	holding reg.	16	RO	0	?	0	Cup2LastError	AuxiliaryFSMs	internal	- // -
100F	holding reg.	16	RO	0	?	0	Cup3LastError	AuxiliaryFSMs	internal	- // -
1010	holding reg.	16	RW	0	?	0	Cup1ErrorStorage	Auxil. Modbus.	user interface	A bitwise OR of all errors for the cup mechanism; can be reset via Modbus
1011	holding reg.	16	RW	0	?	0	Cup2ErrorStorage	Auxil. Modbus.	user interface	- // -
1012	holding reg.	16	RW	0	?	0	Cup3ErrorStorage	Auxil. Modbus.	user interface	- // -

1013	holding reg.	16	RW	1	3	3	InstalledCups	ModbusServer	configuration	The number of Faraday cups to be used
1014	holding reg.	16	RW	1	4	4	ElectrodesInsideCup1	ModbusServer	configuration	The number of electrodes installed in the Faraday cup
1015	holding reg.	16	RW	1	4	4	ElectrodesInsideCup2	ModbusServer	configuration	- // -
1016	holding reg.	16	RW	1	4	4	ElectrodesInsideCup3	ModbusServer	configuration	- // -
1017	holding reg.	16	RW	0	1	0	Cup1Type	ModbusServer	configuration	Type of the Faraday cup; 0 = pneumatic mechanism with 1 limit switch; 1 = motor mechnism with 2 limit switches
1018	holding reg.	16	RW	0	1	0	Cup2Type	ModbusServer	configuration	- // -
1019	holding reg.	16	RW	0	1	1	Cup3Type	ModbusServer	configuration	- // -

101A	holding reg.	16	RW	0	65535	?	Cup1Channel1Gain1Offset	ModbusServer	configuration	The int16 value represents the offset for cups 1–3, channels 1–4, and gains 1–2 (where Gain1 applies to ADC0 and Gain2 applies to ADC1)
101B	holding reg.	16	RW	0	65535	?	Cup1Channel2Gain1Offset	ModbusServer	configuration	- // -
101C	holding reg.	16	RW	0	65535	?	Cup1Channel3Gain1Offset	ModbusServer	configuration	- // -
101D	holding reg.	16	RW	0	65535	?	Cup1Channel4Gain1Offset	ModbusServer	configuration	- // -
101E	holding reg.	16	RW	0	65535	?	Cup2Channel1Gain1Offset	ModbusServer	configuration	- // -
101F	holding reg.	16	RW	0	65535	?	Cup2Channel2Gain1Offset	ModbusServer	configuration	- // -
1020	holding reg.	16	RW	0	65535	?	Cup2Channel3Gain1Offset	ModbusServer	configuration	- // -
1021	holding reg.	16	RW	0	65535	?	Cup2Channel4Gain1Offset	ModbusServer	configuration	- // -
1022	holding reg.	16	RW	0	65535	?	Cup3Channel1Gain1Offset	ModbusServer	configuration	- // -
1023	holding reg.	16	RW	0	65535	?	Cup3Channel2Gain1Offset	ModbusServer	configuration	- // -
1024	holding reg.	16	RW	0	65535	?	Cup3Channel3Gain1Offset	ModbusServer	configuration	- // -
1025	holding reg.	16	RW	0	65535	?	Cup3Channel4Gain1Offset	ModbusServer	configuration	- // -
1026	holding reg.	16	RW	0	65535	?	Cup1Channel1Gain2Offset	ModbusServer	configuration	- // -
1027	holding reg.	16	RW	0	65535	?	Cup1Channel2Gain2Offset	ModbusServer	configuration	- // -
1028	holding reg.	16	RW	0	65535	?	Cup1Channel3Gain2Offset	ModbusServer	configuration	- // -
1029	holding reg.	16	RW	0	65535	?	Cup1Channel4Gain2Offset	ModbusServer	configuration	- // -
102A	holding reg.	16	RW	0	65535	?	Cup2Channel1Gain2Offset	ModbusServer	configuration	- // -
102B	holding reg.	16	RW	0	65535	?	Cup2Channel2Gain2Offset	ModbusServer	configuration	- // -
102C	holding reg.	16	RW	0	65535	?	Cup2Channel3Gain2Offset	ModbusServer	configuration	- // -
102D	holding reg.	16	RW	0	65535	?	Cup2Channel4Gain2Offset	ModbusServer	configuration	- // -
102E	holding reg.	16	RW	0	65535	?	Cup3Channel1Gain2Offset	ModbusServer	configuration	- // -
102F	holding reg.	16	RW	0	65535	?	Cup3Channel2Gain2Offset	ModbusServer	configuration	- // -
1030	holding reg.	16	RW	0	65535	?	Cup3Channel3Gain2Offset	ModbusServer	configuration	- // -
1031	holding reg.	16	RW	0	65535	?	Cup3Channel4Gain2Offset	ModbusServer	configuration	- // -

1032	holding reg.	16	RW	0	65535	?	Cup1Channel1Gain1Factor	ModbusServer	configuration	The uint16 value represents the ratio for cups 1–3, channels 1–4, and gains 1–2 (where Gain1 applies to ADC0 and Gain2 applies to ADC1)
1033	holding reg.	16	RW	0	65535	?	Cup1Channel2Gain1Factor	ModbusServer	configuration	- // -
1034	holding reg.	16	RW	0	65535	?	Cup1Channel3Gain1Factor	ModbusServer	configuration	- // -
1035	holding reg.	16	RW	0	65535	?	Cup1Channel4Gain1Factor	ModbusServer	configuration	- // -
1036	holding reg.	16	RW	0	65535	?	Cup2Channel1Gain1Factor	ModbusServer	configuration	- // -
1037	holding reg.	16	RW	0	65535	?	Cup2Channel2Gain1Factor	ModbusServer	configuration	- // -
1038	holding reg.	16	RW	0	65535	?	Cup2Channel3Gain1Factor	ModbusServer	configuration	- // -
1039	holding reg.	16	RW	0	65535	?	Cup2Channel4Gain1Factor	ModbusServer	configuration	- // -
103A	holding reg.	16	RW	0	65535	?	Cup3Channel1Gain1Factor	ModbusServer	configuration	- // -
103B	holding reg.	16	RW	0	65535	?	Cup3Channel2Gain1Factor	ModbusServer	configuration	- // -
103C	holding reg.	16	RW	0	65535	?	Cup3Channel3Gain1Factor	ModbusServer	configuration	- // -
103D	holding reg.	16	RW	0	65535	?	Cup3Channel4Gain1Factor	ModbusServer	configuration	- // -
103E	holding reg.	16	RW	0	65535	?	Cup1Channel1Gain2Factor	ModbusServer	configuration	- // -
103F	holding reg.	16	RW	0	65535	?	Cup1Channel2Gain2Factor	ModbusServer	configuration	- // -
1040	holding reg.	16	RW	0	65535	?	Cup1Channel3Gain2Factor	ModbusServer	configuration	- // -
1041	holding reg.	16	RW	0	65535	?	Cup1Channel4Gain2Factor	ModbusServer	configuration	- // -
1042	holding reg.	16	RW	0	65535	?	Cup2Channel1Gain2Factor	ModbusServer	configuration	- // -
1043	holding reg.	16	RW	0	65535	?	Cup2Channel2Gain2Factor	ModbusServer	configuration	- // -
1044	holding reg.	16	RW	0	65535	?	Cup2Channel3Gain2Factor	ModbusServer	configuration	- // -
1045	holding reg.	16	RW	0	65535	?	Cup2Channel4Gain2Factor	ModbusServer	configuration	- // -
1046	holding reg.	16	RW	0	65535	?	Cup3Channel1Gain2Factor	ModbusServer	configuration	- // -
1047	holding reg.	16	RW	0	65535	?	Cup3Channel2Gain2Factor	ModbusServer	configuration	- // -
1048	holding reg.	16	RW	0	65535	?	Cup3Channel3Gain2Factor	ModbusServer	configuration	- // -
1049	holding reg.	16	RW	0	65535	?	Cup3Channel4Gain2Factor	ModbusServer	configuration	- // -

104A	holding reg.	16	RW	0	65535	?	RangeChangeThreshold	ModbusServer	configuration	The threshold value for the signal with higher gain (ADC1); if ADC1 is less than RangeChangeThreshold, use ADC1 in the calculation; otherwise, use ADC0 (i.e., the signal with lower gain).

104B	holding reg.	16	RW	0	65535	?	Cup1Channel1LowerLimit	ModbusServer	configuration	- // -
104C	holding reg.	16	RW	0	65535	?	Cup1Channel2LowerLimit	ModbusServer	configuration	- // -
104D	holding reg.	16	RW	0	65535	?	Cup1Channel3LowerLimit	ModbusServer	configuration	- // -
104E	holding reg.	16	RW	0	65535	?	Cup1Channel4LowerLimit	ModbusServer	configuration	- // -
104F	holding reg.	16	RW	0	65535	?	Cup2Channel1LowerLimit	ModbusServer	configuration	- // -
1050	holding reg.	16	RW	0	65535	?	Cup2Channel2LowerLimit	ModbusServer	configuration	- // -
1051	holding reg.	16	RW	0	65535	?	Cup2Channel3LowerLimit	ModbusServer	configuration	- // -
1052	holding reg.	16	RW	0	65535	?	Cup2Channel4LowerLimit	ModbusServer	configuration	- // -
1053	holding reg.	16	RW	0	65535	?	Cup3Channel1LowerLimit	ModbusServer	configuration	- // -
1054	holding reg.	16	RW	0	65535	?	Cup3Channel2LowerLimit	ModbusServer	configuration	- // -
1055	holding reg.	16	RW	0	65535	?	Cup3Channel3LowerLimit	ModbusServer	configuration	- // -
1056	holding reg.	16	RW	0	65535	?	Cup3Channel4LowerLimit	ModbusServer	configuration	- // -

1057	holding reg.	16	RW	0	65535	?	Cup1Channel1UpperLimit	ModbusServer	configuration	- // -
1058	holding reg.	16	RW	0	65535	?	Cup1Channel2UpperLimit	ModbusServer	configuration	- // -
1059	holding reg.	16	RW	0	65535	?	Cup1Channel3UpperLimit	ModbusServer	configuration	- // -
105A	holding reg.	16	RW	0	65535	?	Cup1Channel4UpperLimit	ModbusServer	configuration	- // -
105B	holding reg.	16	RW	0	65535	?	Cup2Channel1UpperLimit	ModbusServer	configuration	- // -
105C	holding reg.	16	RW	0	65535	?	Cup2Channel2UpperLimit	ModbusServer	configuration	- // -
105D	holding reg.	16	RW	0	65535	?	Cup2Channel3UpperLimit	ModbusServer	configuration	- // -
105E	holding reg.	16	RW	0	65535	?	Cup2Channel4UpperLimit	ModbusServer	configuration	- // -
105F	holding reg.	16	RW	0	65535	?	Cup3Channel1UpperLimit	ModbusServer	configuration	- // -
1060	holding reg.	16	RW	0	65535	?	Cup3Channel2UpperLimit	ModbusServer	configuration	- // -
1061	holding reg.	16	RW	0	65535	?	Cup3Channel3UpperLimit	ModbusServer	configuration	- // -
1062	holding reg.	16	RW	0	65535	?	Cup3Channel4UpperLimit	ModbusServer	configuration	- // -

3001	input reg.	16	RO	0	65535	N/A	Cup1Channel1Sample	AnalogInputs	user interface	Raw measurement result
3002	input reg.	16	RO	0	65535	N/A	Cup1Channel2Sample	AnalogInputs	user interface	Raw measurement result
3003	input reg.	16	RO	0	65535	N/A	Cup1Channel3Sample	AnalogInputs	user interface	Raw measurement result
3004	input reg.	16	RO	0	65535	N/A	Cup1Channel4Sample	AnalogInputs	user interface	Raw measurement result
3005	input reg.	16	RO	0	15	N/A	Cup1ChannelError	AnalogInputs	user interface	If the measured value exceeds the limit (Cup1Channel1LowerLimit ..., or Cup1Channel1UpperLimit ...), the corresponding bit is set: bit 0 for channel 1, bit 1 for channel 2, and so on

3006	input reg.	16	RO	0	65535	N/A	Cup2Channel1Sample	AnalogInputs	user interface	Raw measurement result
3007	input reg.	16	RO	0	65535	N/A	Cup2Channel2Sample	AnalogInputs	user interface	Raw measurement result
3008	input reg.	16	RO	0	65535	N/A	Cup2Channel3Sample	AnalogInputs	user interface	Raw measurement result
3009	input reg.	16	RO	0	65535	N/A	Cup2Channel4Sample	AnalogInputs	user interface	Raw measurement result
300A	input reg.	16	RO	0	15	N/A	Cup2ChannelError	AnalogInputs	user interface	similarly as Cup1ChannelError

300B	input reg.	16	RO	0	65535	N/A	Cup3Channel1Sample	AnalogInputs	user interface	Raw measurement result
300C	input reg.	16	RO	0	65535	N/A	Cup3Channel2Sample	AnalogInputs	user interface	Raw measurement result
300D	input reg.	16	RO	0	65535	N/A	Cup3Channel3Sample	AnalogInputs	user interface	Raw measurement result
300E	input reg.	16	RO	0	65535	N/A	Cup3Channel4Sample	AnalogInputs	user interface	Raw measurement result
300F	input reg.	16	RO	0	15	N/A	Cup3ChannelError	AnalogInputs	user interface	similarly as Cup1ChannelError

	sum:	232	B =	00E8	hex