## Sheet1
Address	Type	Bits	RW/RO	Min	Max	Default	Name	Right to modify	Main application	Description

0001	coil	1	RW	false	true	true	Cup1Control	ModbusServer	user interface	Control of Faraday Cup 1 using a pneumatic actuator; true = insert cup; false = withdraw
0002	coil	1	RO	false	true	false		N/A		Reserved
0003	coil	1	RO	false	true	N/A	Cup1Switch	LogicInputs	related to hardware	Measurement of limit switch status; true = switch pressed; false = switch released; in steady state, this status should match the value of register Cup1Control
0004	coil	1	RO	false	true	false		N/A		Reserved

0005	coil	1	RW	false	true	true	Cup2Control	ModbusServer	user interface	Control of Faraday Cup 2 using a pneumatic actuator; true = insert cup; false = withdraw
0006	coil	1	RO	false	true	N/A	ExternalInhibition	LogicInputs	related to hardware	Measurement of the external inhibit logic signal; true = inhibition enabled; false = inhibition disabled
0007	coil	1	RO	false	true	N/A	Cup2Switch	LogicInputs	related to hardware	Measurement of limit switch status; true = switch pressed; false = switch released; in steady state, this status should match the value of register Cup2Control
0008	coil	1	RO	false	true	false		N/A		Reserved

0009	coil	1	RW	false	true	true	Cup3Control	ModbusServer	user interface	Control of Faraday Cup 3 using a motor actuator; true = insert cup; false = withdraw
000A	coil	1	RO	false	true	false		N/A		Reserved
000B	coil	1	RO	false	true	N/A	Cup3Switch1	LogicInputs	related to hardware	Measurement of limit switch status; true = switch pressed; false = switch released; in steady state, this status should be equal to the negation of register Cup3Control
000C	coil	1	RO	false	true	N/A	Cup3Switch2	LogicInputs	related to hardware	Measurement of limit switch status; true = switch pressed; false = switch released; in steady state, this status should match the value of register Cup3Control

0100	coil	1	RO	false	true	N/A	Cup1RequestedState	MainFSM	internal	Command for the AuxiliaryFSM; true = insert the cup; false = withdraw the cup
0101	coil	1	RO	false	true	N/A	Cup2RequestedState	MainFSM	internal	- // -
0102	coil	1	RO	false	true	N/A	Cup3RequestedState	MainFSM	internal	- // -

0110	coil	1	RO	false	true	N/A	Cup1Steady	AuxiliaryFSMs	internal	Check whether the mechanism of the cup is in a transient state; true = steady state; false = transient state
0111	coil	1	RO	false	true	N/A	Cup2Steady	AuxiliaryFSMs	internal	- // -
0112	coil	1	RO	false	true	N/A	Cup3Steady	AuxiliaryFSMs	internal	- // -
0113	coil	1	RO	false	true	N/A	Cup1Inserted	AuxiliaryFSMs	user interface	Status of the cup; true = inserted; false = withdrawn
0114	coil	1	RO	false	true	N/A	Cup2Inserted	AuxiliaryFSMs	user interface	- // -
0115	coil	1	RO	false	true	N/A	Cup3Inserted	AuxiliaryFSMs	user interface	- // -

1000	holding reg.	16	RO	0	?	0	ErrorCode	MainFSM	user interface	Error code for the entire device (bitmap)
1001	holding reg.	16	RO	0	?	0	LastError	MainFSM	user interface	Code of the last error
1002	holding reg.	16	RW	0	?	0	ErrorStorage	MainFSM, Modbus.	user interface	A bitwise OR of all errors; can be reset via Modbus

1010	holding reg.	16	RW	1	65535	?	TimeLimitInserting1	ModbusServer	configuration	Time limit for the transient state when inserting a Faraday cup
1011	holding reg.	16	RW	1	65535	?	TimeLimitInserting2	ModbusServer	configuration	- // -
1012	holding reg.	16	RW	1	65535	?	TimeLimitInserting3	ModbusServer	configuration	- // -
1013	holding reg.	16	RW	1	65535	?	TimeLimitWithdrawing1	ModbusServer	configuration	Time limit for the transient state when withdrawing a Faraday cup
1014	holding reg.	16	RW	1	65535	?	TimeLimitWithdrawing2	ModbusServer	configuration	- // -
1015	holding reg.	16	RW	1	65535	?	TimeLimitWithdrawing3	ModbusServer	configuration	- // -

1020	holding reg.	16	RW	1	3	1	ActiveCup	MainFSM	internal	The first inserted Faraday cup as seen from the ion source side; if none is inserted, the previous value should be retained;

1030	holding reg.	16	RO	0	?	0	Cup1Error	AuxiliaryFSMs	internal	Error code for the cup mechanism (bitmap)
1031	holding reg.	16	RO	0	?	0	Cup2Error	AuxiliaryFSMs	internal	- // -
1032	holding reg.	16	RO	0	?	0	Cup3Error	AuxiliaryFSMs	internal	- // -
1033	holding reg.	16	RO	0	?	0	Cup1LastError	AuxiliaryFSMs	internal	Code of the last error for the cup mechanism
1034	holding reg.	16	RO	0	?	0	Cup2LastError	AuxiliaryFSMs	internal	- // -
1035	holding reg.	16	RO	0	?	0	Cup3LastError	AuxiliaryFSMs	internal	- // -
1036	holding reg.	16	RW	0	?	0	Cup1ErrorStorage	Auxil. Modbus.	user interface	A bitwise OR of all errors for the cup mechanism; can be reset via Modbus
1037	holding reg.	16	RW	0	?	0	Cup2ErrorStorage	Auxil. Modbus.	user interface	- // -
1038	holding reg.	16	RW	0	?	0	Cup3ErrorStorage	Auxil. Modbus.	user interface	- // -

1100	holding reg.	16	RW	1	3	3	InstalledCups	ModbusServer	configuration	The number of Faraday cups to be used
1101	holding reg.	16	RW	1	4	4	ElectrodesInsideCup1	ModbusServer	configuration	The number of electrodes installed in the Faraday cup
1102	holding reg.	16	RW	1	4	4	ElectrodesInsideCup2	ModbusServer	configuration	- // -
1103	holding reg.	16	RW	1	4	4	ElectrodesInsideCup3	ModbusServer	configuration	- // -
1104	holding reg.	16	RW	0	1	0	Cup1Type	ModbusServer	configuration	Type of the Faraday cup; 0 = pneumatic mechanism with 1 limit switch; 1 = motor mechnism with 2 limit switches
1105	holding reg.	16	RW	0	1	0	Cup2Type	ModbusServer	configuration	- // -
1106	holding reg.	16	RW	0	1	1	Cup3Type	ModbusServer	configuration	- // -

1200	holding reg.	16	RW	0	65535	?	Cup1Channel1Gain1Offset	ModbusServer	configuration	The int16 value represents the offset for cups 1–3, channels 1–4, and gains 1–2 (where Gain1 applies to ADC0 and Gain2 applies to ADC1)
1201	holding reg.	16	RW	0	65535	?	Cup1Channel2Gain1Offset	ModbusServer	configuration	- // -
1202	holding reg.	16	RW	0	65535	?	Cup1Channel3Gain1Offset	ModbusServer	configuration	- // -
1203	holding reg.	16	RW	0	65535	?	Cup1Channel4Gain1Offset	ModbusServer	configuration	- // -
1204	holding reg.	16	RW	0	65535	?	Cup2Channel1Gain1Offset	ModbusServer	configuration	- // -
1205	holding reg.	16	RW	0	65535	?	Cup2Channel2Gain1Offset	ModbusServer	configuration	- // -
1206	holding reg.	16	RW	0	65535	?	Cup2Channel3Gain1Offset	ModbusServer	configuration	- // -
1207	holding reg.	16	RW	0	65535	?	Cup2Channel4Gain1Offset	ModbusServer	configuration	- // -
1208	holding reg.	16	RW	0	65535	?	Cup3Channel1Gain1Offset	ModbusServer	configuration	- // -
1209	holding reg.	16	RW	0	65535	?	Cup3Channel2Gain1Offset	ModbusServer	configuration	- // -
120A	holding reg.	16	RW	0	65535	?	Cup3Channel3Gain1Offset	ModbusServer	configuration	- // -
120B	holding reg.	16	RW	0	65535	?	Cup3Channel4Gain1Offset	ModbusServer	configuration	- // -
120C	holding reg.	16	RW	0	65535	?	Cup1Channel1Gain2Offset	ModbusServer	configuration	- // -
120D	holding reg.	16	RW	0	65535	?	Cup1Channel2Gain2Offset	ModbusServer	configuration	- // -
120E	holding reg.	16	RW	0	65535	?	Cup1Channel3Gain2Offset	ModbusServer	configuration	- // -
120F	holding reg.	16	RW	0	65535	?	Cup1Channel4Gain2Offset	ModbusServer	configuration	- // -
1210	holding reg.	16	RW	0	65535	?	Cup2Channel1Gain2Offset	ModbusServer	configuration	- // -
1211	holding reg.	16	RW	0	65535	?	Cup2Channel2Gain2Offset	ModbusServer	configuration	- // -
1212	holding reg.	16	RW	0	65535	?	Cup2Channel3Gain2Offset	ModbusServer	configuration	- // -
1213	holding reg.	16	RW	0	65535	?	Cup2Channel4Gain2Offset	ModbusServer	configuration	- // -
1214	holding reg.	16	RW	0	65535	?	Cup3Channel1Gain2Offset	ModbusServer	configuration	- // -
1215	holding reg.	16	RW	0	65535	?	Cup3Channel2Gain2Offset	ModbusServer	configuration	- // -
1216	holding reg.	16	RW	0	65535	?	Cup3Channel3Gain2Offset	ModbusServer	configuration	- // -
1217	holding reg.	16	RW	0	65535	?	Cup3Channel4Gain2Offset	ModbusServer	configuration	- // -

1240	holding reg.	16	RW	0	65535	?	Cup1Channel1Gain1Factor	ModbusServer	configuration	The uint16 value represents the ratio for cups 1–3, channels 1–4, and gains 1–2 (where Gain1 applies to ADC0 and Gain2 applies to ADC1)
1241	holding reg.	16	RW	0	65535	?	Cup1Channel2Gain1Factor	ModbusServer	configuration	- // -
1242	holding reg.	16	RW	0	65535	?	Cup1Channel3Gain1Factor	ModbusServer	configuration	- // -
1243	holding reg.	16	RW	0	65535	?	Cup1Channel4Gain1Factor	ModbusServer	configuration	- // -
1244	holding reg.	16	RW	0	65535	?	Cup2Channel1Gain1Factor	ModbusServer	configuration	- // -
1245	holding reg.	16	RW	0	65535	?	Cup2Channel2Gain1Factor	ModbusServer	configuration	- // -
1246	holding reg.	16	RW	0	65535	?	Cup2Channel3Gain1Factor	ModbusServer	configuration	- // -
1247	holding reg.	16	RW	0	65535	?	Cup2Channel4Gain1Factor	ModbusServer	configuration	- // -
1248	holding reg.	16	RW	0	65535	?	Cup3Channel1Gain1Factor	ModbusServer	configuration	- // -
1249	holding reg.	16	RW	0	65535	?	Cup3Channel2Gain1Factor	ModbusServer	configuration	- // -
124A	holding reg.	16	RW	0	65535	?	Cup3Channel3Gain1Factor	ModbusServer	configuration	- // -
124B	holding reg.	16	RW	0	65535	?	Cup3Channel4Gain1Factor	ModbusServer	configuration	- // -
124C	holding reg.	16	RW	0	65535	?	Cup1Channel1Gain2Factor	ModbusServer	configuration	- // -
124D	holding reg.	16	RW	0	65535	?	Cup1Channel2Gain2Factor	ModbusServer	configuration	- // -
124E	holding reg.	16	RW	0	65535	?	Cup1Channel3Gain2Factor	ModbusServer	configuration	- // -
124F	holding reg.	16	RW	0	65535	?	Cup1Channel4Gain2Factor	ModbusServer	configuration	- // -
1250	holding reg.	16	RW	0	65535	?	Cup2Channel1Gain2Factor	ModbusServer	configuration	- // -
1251	holding reg.	16	RW	0	65535	?	Cup2Channel2Gain2Factor	ModbusServer	configuration	- // -
1252	holding reg.	16	RW	0	65535	?	Cup2Channel3Gain2Factor	ModbusServer	configuration	- // -
1253	holding reg.	16	RW	0	65535	?	Cup2Channel4Gain2Factor	ModbusServer	configuration	- // -
1254	holding reg.	16	RW	0	65535	?	Cup3Channel1Gain2Factor	ModbusServer	configuration	- // -
1255	holding reg.	16	RW	0	65535	?	Cup3Channel2Gain2Factor	ModbusServer	configuration	- // -
1256	holding reg.	16	RW	0	65535	?	Cup3Channel3Gain2Factor	ModbusServer	configuration	- // -
1257	holding reg.	16	RW	0	65535	?	Cup3Channel4Gain2Factor	ModbusServer	configuration	- // -

1280	holding reg.	16	RW	0	65535	?	RangeChangeThreshold	ModbusServer	configuration	The threshold value for the signal with higher gain (ADC1); if ADC1 is less than RangeChangeThreshold, use ADC1 in the calculation; otherwise, use ADC0 (i.e., the signal with lower gain).

12A0	holding reg.	16	RW	0	65535	?	Cup1Channel1LowerLimit	ModbusServer	configuration	- // -
12A1	holding reg.	16	RW	0	65535	?	Cup1Channel2LowerLimit	ModbusServer	configuration	- // -
12A2	holding reg.	16	RW	0	65535	?	Cup1Channel3LowerLimit	ModbusServer	configuration	- // -
12A3	holding reg.	16	RW	0	65535	?	Cup1Channel4LowerLimit	ModbusServer	configuration	- // -
12A4	holding reg.	16	RW	0	65535	?	Cup2Channel1LowerLimit	ModbusServer	configuration	- // -
12A5	holding reg.	16	RW	0	65535	?	Cup2Channel2LowerLimit	ModbusServer	configuration	- // -
12A6	holding reg.	16	RW	0	65535	?	Cup2Channel3LowerLimit	ModbusServer	configuration	- // -
12A7	holding reg.	16	RW	0	65535	?	Cup2Channel4LowerLimit	ModbusServer	configuration	- // -
12A8	holding reg.	16	RW	0	65535	?	Cup3Channel1LowerLimit	ModbusServer	configuration	- // -
12A9	holding reg.	16	RW	0	65535	?	Cup3Channel2LowerLimit	ModbusServer	configuration	- // -
12AA	holding reg.	16	RW	0	65535	?	Cup3Channel3LowerLimit	ModbusServer	configuration	- // -
12AB	holding reg.	16	RW	0	65535	?	Cup3Channel4LowerLimit	ModbusServer	configuration	- // -

12B0	holding reg.	16	RW	0	65535	?	Cup1Channel1UpperLimit	ModbusServer	configuration	- // -
12B1	holding reg.	16	RW	0	65535	?	Cup1Channel2UpperLimit	ModbusServer	configuration	- // -
12B2	holding reg.	16	RW	0	65535	?	Cup1Channel3UpperLimit	ModbusServer	configuration	- // -
12B3	holding reg.	16	RW	0	65535	?	Cup1Channel4UpperLimit	ModbusServer	configuration	- // -
12B4	holding reg.	16	RW	0	65535	?	Cup2Channel1UpperLimit	ModbusServer	configuration	- // -
12B5	holding reg.	16	RW	0	65535	?	Cup2Channel2UpperLimit	ModbusServer	configuration	- // -
12B6	holding reg.	16	RW	0	65535	?	Cup2Channel3UpperLimit	ModbusServer	configuration	- // -
12B7	holding reg.	16	RW	0	65535	?	Cup2Channel4UpperLimit	ModbusServer	configuration	- // -
12B8	holding reg.	16	RW	0	65535	?	Cup3Channel1UpperLimit	ModbusServer	configuration	- // -
12B9	holding reg.	16	RW	0	65535	?	Cup3Channel2UpperLimit	ModbusServer	configuration	- // -
12BA	holding reg.	16	RW	0	65535	?	Cup3Channel3UpperLimit	ModbusServer	configuration	- // -
12BB	holding reg.	16	RW	0	65535	?	Cup3Channel4UpperLimit	ModbusServer	configuration	- // -

3001	input reg.	16	RO	0	65535	N/A	Cup1Channel1Sample	AnalogInputs	user interface	Raw measurement result
3002	input reg.	16	RO	0	65535	N/A	Cup1Channel2Sample	AnalogInputs	user interface	Raw measurement result
3003	input reg.	16	RO	0	65535	N/A	Cup1Channel3Sample	AnalogInputs	user interface	Raw measurement result
3004	input reg.	16	RO	0	65535	N/A	Cup1Channel4Sample	AnalogInputs	user interface	Raw measurement result
3005	input reg.	16	RO	0	15	N/A	Cup1ChannelError	AnalogInputs	user interface	If the measured value exceeds the limit (Cup1Channel1LowerLimit ..., or Cup1Channel1UpperLimit ...), the corresponding bit is set: bit 0 for channel 1, bit 1 for channel 2, and so on

3011	input reg.	16	RO	0	65535	N/A	Cup2Channel1Sample	AnalogInputs	user interface	Raw measurement result
3012	input reg.	16	RO	0	65535	N/A	Cup2Channel2Sample	AnalogInputs	user interface	Raw measurement result
3013	input reg.	16	RO	0	65535	N/A	Cup2Channel3Sample	AnalogInputs	user interface	Raw measurement result
3014	input reg.	16	RO	0	65535	N/A	Cup2Channel4Sample	AnalogInputs	user interface	Raw measurement result
3015	input reg.	16	RO	0	15	N/A	Cup2ChannelError	AnalogInputs	user interface	similarly as Cup1ChannelError

3021	input reg.	16	RO	0	65535	N/A	Cup3Channel1Sample	AnalogInputs	user interface	Raw measurement result
3022	input reg.	16	RO	0	65535	N/A	Cup3Channel2Sample	AnalogInputs	user interface	Raw measurement result
3023	input reg.	16	RO	0	65535	N/A	Cup3Channel3Sample	AnalogInputs	user interface	Raw measurement result
3024	input reg.	16	RO	0	65535	N/A	Cup3Channel4Sample	AnalogInputs	user interface	Raw measurement result
3025	input reg.	16	RO	0	15	N/A	Cup3ChannelError	AnalogInputs	user interface	similarly as Cup1ChannelError

	sum:	232	B